## Instructions
Electrical Load Estimator Tool Instructions
Introduction & Disclaimer
Two calculators are provided that can be used for determining the adequacy of existing service capacity when new electric appliances are added to the household, for example an electric vehicle charger, a heat pump water heater, or other changes that affect the load. The accuracy of these calculators is subject to the correctness of the data entered, carries no implied guarantee, and is entirely at the user's risk. Applicable load calculation guidance within the California Electrical Code (CEC; Title 24, Part 3) sections 220.82, 220.83, and 220.87 has not changed between 2022 and 2025 code cycles; this estimator is applicable under both codes through 12/31/2028. The Maximum Existing Load calculator is based on California Electrical Code (CEC) Section 220.87 – Determining Existing Loads. It uses actual loads instead of completing an accounting of connected loads and is therefore simpler and more accurate. This method requires access to the homeowner’s utility account for obtaining the maximum demand over a one-year period. This code section also requires that overload and overcurrent protection be provided in accordance with CEC Sections 230.90 and 240.4 respectively, which is typically included when the service is originally installed. This method must not be used if the home has been equipped with a photovoltaic and/or home battery system since they will reduce the measured power and are subject to disconnection or failure. The Service Load Calculation is based on CEC Section 220.82 – Dwelling Unit, which is designed for sizing new services. However, it can be used for additions to existing services (normally covered by Section 220.83 – Existing Dwelling Unit). This calculator includes typical appliance loads which facilitates the calculations. However, if actual loads differ from the entered default values the correct values should be used. The nameplate ratings for all appliances including cooking, laundry, and water heaters that are fastened in place or permanently connected should be verified. This method is best used by or under the guidance of an electrical engineer, electrical contractor, the building official, or other building professionals familiar with the electrical code.
Instructions - Maximum Existing Load Method (CEC Section 220.87)
1. Under the Maximum Existing Load Tab, in the table enter the Rated Amps of the Existing Service. This can be found on a label on the main breaker panel serving the house, where the meter is located.
2. In the same table, enter the Maximum Existing Demand which can be obtained as follows:
a. Go to PGE.com and sign into the account associated with the service.
b. In the Usage, Rates & Savings box select “ENERGY USE DETAILS”
c. Scroll to the bottom of the graph and click on the Green Button ("download my data")
d. Select “CSV” for the data format
e. Select “Export usage for a range of days” and choose data from the previous year (no new loads should have been added in the current year).
f. Press “EXPORT”
g. Double-click on the downloaded "pge_electric_interval_data" file, which should open it in Excel.
h. In the cell above the USAGE column (E5) enter =max( then click on the first kWh value in the column. While holding down the Shift key, press End then ▼on your keyboard to select the entire column and press Enter.
i. The load in Kilowatts for the "Highest Usage Hour" will be shown in the selected cell (E5). Enter this under the Maximum Existing Load tab (F16).
3. Obtain the total new load to be added to the service in Watts. If it is only available in Amps, multiply by 240 to convert it to V-A, and enter it in the New Added Load cell of the table.
4. Read the Total Current Demand from the table. If it is larger than the Existing Service Amps the last cell in the table will indicate that a service upgrade is required.
Instructions - Service Load Calculation Method (CEC Section 220.83)
The orange shaded cells are for entering information such as the quantity of appliances and nameplate ratings. The values provided in those cells are for example purposes only and should be deleted or changed as appropriate. It is especially important to enter correct values for Cooling System and Heat Pump nameplate watts. If only the amps are listed on nameplate, then enter the product of the amps and the voltage listed on the nameplate (V-A). The default watt values in the blue shaded cells should only be modified if nameplate values are known. For accuracy, nameplate values should be verified for all appliances. If the existing values are changed the cell shading will turn to green to indicate the change. All unshaded cells contain calculated values and cannot be modified.
1. Under General Lighting/Power Load enter:
a. The total square footage of the building based on the outside dimensions of the dwelling unit. It shall not include garages or unused spaces not adaptable for future use.
b. The number of individual circuits serving the kitchen. This may be determined from circuit breaker labeling, or by switching breakers on and off.
c. The number of circuits serving the laundry room, not including those serving washers and clothes dryers (typically one).
2. Under Appliances and Equipment:
a. Enter the quantity of each permanently installed appliance. If the listed appliance is not present leave the cell blank. If there are appliances not included in the list, enter them under Appliance Name, replacing “Other”.
b. Review the nameplate watts (or V-A) of each appliance present and if it differs from the value in the Default column, enter the correct value.
c. Note that the General and Appliance Loads are automatically tallied. The Effective General Load is the subtotal less 10,000 with 40% of the remainder added. (This accounts for diversity of use.)
3. Under Heating and Air-Conditioning, enter:
a. The nameplate amps of the outdoor compressor unit(s) in the blanks provided. If there are more than one, enter the quantity and total amps.
b. If a heat pump is installed and includes a resistance or “strip” heater, enter the watts of the heater. This is typically located at the air supply end of the indoor air handler and provides supplemental heating if the heat pump cannot keep up with the heating load, and when the heat pump enters a defrost cycle.
4. To the right of the cell labeled Rating of Existing Electric Service and Panel enter the rated service amps that is listed on the main breaker panel near the meter.
5. Read the Total Amps required for the service conductors and panel. If the total is greater than the rating of the existing service and panel, the last cell in the spreadsheet will indicate that a service upgrade is required (Yes or No).

## Maximum Existing Load
Maximum Existing Load Calculator
These Load Calculations are in accordance with California Electrical Code Section 220.87 - Determining Existing Loads
• Refer to the instructions, which describe how to obtain the Maximun Existing Demand. • Entries in the orange cells are for example purposes only and should be over-writen with the correct data. • If a photovoltaic system or vehicle charger is to be added, or if the house is already equipped with a PV and/or battery system, use the Service Load Calculation Method.
Key: | Fixed Inputs
User inputs
Calculated Values
| Service Nominal Voltage (V) : | 240
| Enter the Rated Amps of the Existing Service here -> | 125
| Enter the load for the Highest Usage Hour from PG&E data here -> | 19
| Maximum demand at 125% (Watts) = | 23750
| New added load (in Watts or Volts x Amps) -> | 3000
| Total New Load (Watts) = | 26750
| Total Current Demand (Amps) = | 111.4583
| Service Upgrade Required: | no

## Service Load Calculation
These Load Calculations are based on California Electrical Code Section 220.82 - Dwelling Unit
• Refer to Instructions. • User inputs are only allowed in the orange-shaded cells, and in the blue-shaded cells if nameplate values are different than those listed. Other cells are automatically filled. • The existing entries in the orange cells are for example purposes only and should be deleted or over-written.
Applicable Equipment | Description of Load |  |  | Default Value (measured in Watts) | Nameplate Rating (measured in Watts) | Applicable Rating (measured in Watts) | Units
General Lighting/Power Load
Required | Insert Total sq. footage of building -> | 1700 |  | Multiply square footage by VA/(ft2)-> | 3 | 5100 | Watts
Required | Insert # of Kitchen Circuits -> | 2 |  | Mutiply # by volt-amps/circuit -> | 1500 | 3000 | Watts
Required | Insert # of Laundry Circuits -> | 1 |  | Mutiply # by volt-amps/circuit -> | 1500 | 1500 | Watts
Subtotal | [5 empty] | 9600 | Watts
Appliances and Equipment Excluding Air Conditioners and Space Heaters |  |  |  | Default | Nameplate Rating | Applicable Rating
Instruction below
Enter Quantity | Appliance Name |  |  | Default Value (measured in Watts) | If namelplate rating is diferent than Default Value, replace with nameplate ratiing | Max Default Value or User Inserted Value | Units
| Microwave |  |  | 1400 |  |  | Watts
| Trash Compactor |  |  | 1000 |  |  | Watts
1 | Dishwasher |  |  | 1500 | 1500 | 1500 | Watts
| Disposal |  |  | 1000 |  |  | Watts
| Electric Wall Oven |  |  | 2000 |  |  | Watts
| Electric/Induction Cooktop |  |  | 1800 |  |  | Watts
1 | Electric Range (5 kW for induction, 10 kW for resistance) |  |  | 10000 | 5000 | 5000 | Watts
1 | Electric Clothes Dryer that is not connected to the laundry branch circuit |  |  | 4000 | 4000 | 4000 | Watts
| Electric Heat Pump Clothes Dryer |  |  | 1800 |  |  | Watts
| Electric Clothes Washer |  |  | 500 |  |  | Watts
| Electric Tankless Water Heater |  |  | 15000 |  |  | Watts
| Electric Water Heater |  |  | 4000 |  |  | Watts
| Electric Heat Pump Water Heater |  |  | 550 |  |  | Watts
| Level 2 Electric Vehicle Supply Equipment (EVSE) (Required for new homes) |  |  | 7000 |  |  | Watts
| Evaporative Cooler |  |  | 500 |  |  | Watts
| Pool or Spa |  |  | 2000 |  |  | Watts
| Other |  |  | n/a |  |  | Watts
| Other |  |  | n/a |  |  | Watts
| Other |  |  | n/a |  |  | Watts
Subtotal (Appliance and Equipment) | [5 empty] | 10500 | Watts
Total (General Lighting/Power Load + Appliance and Equipment) | [5 empty] | 20100 | Watts
Calculation of General and Appliance Load (load in excess of 10,000 W is counted at 40%)
Subtotal (A) = Total Watts - 10,000 VA | [5 empty] | 10100 | Watts
Subtotal (B) = Subtotal (A) x .40 | [5 empty] | 4040 | Watts
Effective General Load = Subtotal (B) + 10,000 VA | [5 empty] | 14040 | Watts
Heating and Air-Conditioning Load (Include the largest of the following)
Central Cooling System (outdoor units only) |  | Total Nameplate Amps: |  | 240 Volts |  | 0 | V-A
Heat Pumps (outdoor units only) |  | Total Nameplate Amps: | 29 | 240 Volts |  | 6960 | V-A
Heat Pump Supplemental Resistance Heat (if installed) |  | Total Nameplate Watts: | 5000 | 240 Volts |  | 5000 | V-A
Heat Pump Total Effective Demand |  | 100% of heat pump demand plus 65% of strip heat demand |  |  |  | 10210 | V-A
Permanently Connected Electric Resistance Space Heaters |  | Quantity: | Total Nameplate Watts: |  | Effective Demand: | 0 | Watts
HVAC Load - Greater of Space Heating and Cooling Demand | [5 empty] | 10210 | VA or W
Total Load = Highest HVAC Load + General Load | [5 empty] | 24250 | VA or W
Total Current Load Divided by 240 Volts | [5 empty] | 101.0417 | A
40 Amp Back-feed protection for future Photovoltaic System if present or to be added | [5 empty] | 40 | A
Total Amps required for Service Conductors and Panel = | [5 empty] | 141.0417 | A
Rating of Existing Electric Service and Panel (Amps) = | [5 empty] | 150 | A
Service/Panel Upgrade Required? (Yes ¦ No) | [5 empty] | No